## Slide 1: OT Security Assessment & Analysis Sample Report
Notes: This briefing pack will describe at a high level approach to assisting clients address the Operational Technology (OT) and Internet of Things (IoT) security challenge.

## Slide 2: Activity Summary
PCAP files based analysis
85GB of traffic
Discovered 925 devices
  Avg. traffic ~6 Mb/s

## Slide 3: Executive Summary – Main Findings
Item | System’s Findings
Asset Inventory | A total of 925 devices were automatically discovered, including PLCs, IP cameras and servers.
Anomaly and threat detection | Internet connection & Remote Control applications Internet-connected Industrial asset (Rockwell) Multiple scanning attempts PLC not responding
Vulnerability detection | Default SNMP password Unsecure protocols: Telnet and HTTP SMBv1 (WannaCry vulnerability) Multihomed device risk Skype application Windows XP is in use
PLC/Software Vulnerabilities | Available using passive mode (requires software versions to be seen in network) or Active Mode (polling)
Network Architecture Security Review | Using Exposure Analysis tool – requires a 1-hour meeting w/ customer for review.

## Slide 4: Automatic Asset Inventory and Management

## Slide 5: Network Architecture Mapping
Logical Topology
Subnet Topology
Physical Network View

## Slide 6: Network Architecture Conclusions
The network is highly connected as a result of:
  Default discovery protocols that were left on
    LDAP
  Misconfigured/scanning applications
    15540/TCP (“essprotect”)
    NTP
The current network design isn’t clear
Conclusion: a 1-hour network architecture review w/ the customer is required in order to define Exposure Groups and analyze the findings.

## Slide 7: Industrial Protocol Visibility & Security

## Slide 8: Major Findings

## Slide 9: Finding #1 – Internet Connections & Remote Control (AnyDesk)
Many hosts have external connections to the Internet.
Risk – Exposing the OT network to internet threats and malware.
# External Connections
AnyDesk Remote Control

## Slide 10: Finding #2 –Multiple scanning attempts
Multiple hosts were seen scanning the network.
Risk – Indicates a misconfiguration (automated discovery of network services). Can cause industrial devices to stop responding.
Example - Some industrial devices pose a limit on the number of open sockets. When scanned, the limit is exhausted, and device connectivity is disrupted.

## Slide 11: Finding #3 – Default SNMP password
Hosts using the default SNMP password to perform read and write operations.
Risk – Attackers or malware may use default credentials to read or modify device configurations.

## Slide 12: Finding #4 – Unsecure Protocols
Unsecure plaintext protocols are in use.
Risk: Password theft, man-in-the-middle.

## Slide 13: Finding #5 - SMB version 1
Legacy version of SMB is in use.
Risk: WannaCry and other malware infection.

## Slide 14: Finding #6 – Multihomed device risk
Multiple devices using more than one network interface.
Risk: Firewall bypass, malware propagation between network segments.

## Slide 15: Finding #7– Skype Application
The Microsoft Skype application was detected on a workstation.
Risk: The application might give remote control over the computer, consume significant bandwidth, or allow users to transfer files in an unmonitored manner.
Example of a Skype Vulnerability

## Slide 16: Finding #8– Windows XP is in Use
Windows XP has been detected in the network.
Risk: Windows XP is no longer supported by Microsoft, which exposes it to cyber attacks.

## Slide 17: Finding #9– Internet-Connected Industrial Asset
A Rockwell industrial device is communicating with the Internet.
Risk: Malicious traffic originating from the internet may impact the device and result in severe consequences to production processes.

## Slide 18: Finding #10 – PLC Not Responding
A service on a PLC did not respond to a request by a workstation.
Risk: Disruption to production process or production monitoring.

## Slide 19: Additional Findings
Hostname and IP conflicts
DHCP misconfiguration

## Slide 20: IEC 62443 Compliance
Per site risk scoring and trends over time
Per site detailed compliance reports
Based on actual network traffic
Client Site 1

## Slide 21: System Analysis Conclusions
Not everything can be fixed
OT networks have security limitations: difficulty patching, insecure protocols, etc.
Therefore: Real-time malware and anomaly detection is critical to prevent incidents.
The network is dynamic and highly connected
High probability of new risks appearing over time.
Therefore: Real-time risk reporting is important to maintain reasonable risk levels.

## Slide 22: Recommended Next Steps
Define security best-practices
  Access control, protocols usage, password policy, and more.
Deploy industrial cyber management platform
  Incident detection & vulnerability management
  Network architecture review using Exposure Analysis tool
Establish incident handling process
Establish central governance to adhere to organizational cyber security policy